## Data collection
5 hours = 60, 1 hour = 12
[7 empty] | COMMENTS | IF 10 GPM:
| T |  |  | P |  |  | full fire, 1/8 splits - all dry to 15% outside temp 30 F - short citcuit through garden hose in barn, pump medium setting
Time | manif inlet | manif outlet | delta T | suc pump | Pump status | Fan Status | (suc pump P is pre Y-Strainer) masonry was at 85F, tank was at 83F before starting | 0
2.2 | 44 | 65 | 21 | 10 | 0 | 0 | FIRE IGNITED first run uninsulated tank/boiler - prelim BTU/Hr calcs | 0
2.25 | 44 | 85 | 41 | 10 | 0 | 0 | fire rages, bell damper closed at 3 minutes into burn | 0
2.3 | 59 | 165 | 106 | 5 | 1 | 0 | pump on 145 F at 2:29 spike to | 0
2.35 | 82 | 100 | 18 | 5 | 1 | 0 |  | 50
2.4 | 83 | 100 | 17 | 5 | 1 | 0 |  | 100
2.45 | 87 | 98 | 11 | 5 | 1 | 0 |  | 150
2.5 | 88 | 97 | 9 | 5 | 1 | 0 |  | 200
2.55 | 89 | 96 | 7 | 5 | 1 | 0 |  | 250
3 | 89 | 96 | 7 | 5 | 1 | 0 |  | 300
3.05 | 90 | 96 | 6 | 5 | 1 | 0 |  | 350
3.1 | 90 | 95 | 5 | 5 | 1 | 0 |  | 400
3.15 | 90 | 94 | 4 | 5 | 1 | 0 |  | 450
3.2 | 90 | 93 | 3 | 5 | 1 | 0 | closed flu damper at 3:20 | 500
3.25 | 91 | 91 | 0 | 5 | 1 | 0 |  | 550
3.3 | 91 | 98 | 7 | 8 | 0 | 0 | Pump kicked off at 3:29 | 600
3.35 | 91 | 100 | 9 | 5 | 1 | 0 | Exit reading spiked to 115 F before pump came on again | 650
3.4 | 90 | 91 | 1 | 8 | 0 | 0 | pump kicked off at 3:39 | 700
3.45 | 89 | 110 | 21 | 5 | 1 | 0 | fire reloaded and ignited - 2/3 size of original burn, also greener wood, | 750
3.5 | 90 | 100 | 10 | 5 | 1 | 0 |  | 800
3.55 | 94 | 110 | 16 | 5 | 1 | 0 |  | 850
4 | 96 | 112 | 16 | 5 | 1 | 0 |  | 900
4.05 | 98 | 111 | 13 | 5 | 1 | 0 |  | 950
4.1 | 100 | 111 | 11 | 5 | 1 | 0 |  | 1000
4.15 | 101 | 113 | 12 | 5 | 1 | 0
4.2 | 102 | 112 | 10 | 5 | 1 | 0
4.25 | 103 | 112 | 9 | 5 | 1 | 0
4.3 | 103 | 112 | 9 | 5 | 1 | 0
4.35 | 104 | 113 | 9 | 5 | 1 | 0
4.4 | 105 | 114 | 9 | 5 | 1 | 0
4.45 | 106 | 114 | 8 | 5 | 1 | 0
4.5 | 107 | 113 | 6 | 5 | 1 | 0
4.55 | 108 | 113 | 5 | 5 | 1 | 0
5 | 109 | 112 | 3 | 5 | 1 | 0
5.05 | 109 | 112 | 3 | 5 | 1 | 0
5.1 | 110 | 113 | 3 | 5 | 1 | 0
5.15 | 110 | 113 | 3 | 5 | 1 | 0
5.2 | 110 | 113 | 3 | 5 | 1 | 0
5.25 | 111 | 113 | 2 | 5 | 1 | 0
5.3 | 111 | 114 | 3 | 5 | 1 | 0
5.35 | 111 | 113 | 2 | 5 | 1 | 0
5.4 | 111 | 113 | 2 | 5 | 1 | 0
5.45 | 111 | 112 | 1 | 5 | 1 | 0
5.5 | 111 | 112 | 1 | 5 | 1 | 0 | new fire built. filled the box - about 20 eighths 18" avg Length
5.55 | 111 | 125 | 14 | 5 | 1 | 0
6 | 112 | 136 | 24 | 5 | 1 | 0
6.05 | 115 | 145 | 30 | 6 | 1 | 0 | noting a smell - cardboard? also drips are dripping a little more.
6.1 | 118 | 145 | 27 | 6 | 1 | 0
6.15 | 121 | 145 | 24 | 6 | 1 | 0
6.2 | 124 | 144 | 20 | 6 | 1 | 0
6.25 | 125 | 144 | 19 | 4 | 1 | 0 | turning on unit hearer for five minutes after this reading
6.3 | 126 | 144 | 18 | 4 | 1 | 1 | unit heater on for five minutes - full flow to unit heater
6.35 | 127 | 142 | 15 | 5 | 1 | 0 | opened to split flow between unit heater and straight to tank
6.4 | 129 | 141 | 12 | 5 | 1 | 0
6.45 | 130 | 140 | 10 | 5 | 1 | 0
6.5 | 130 | 140 | 10 | 5 | 1 | 0
7 | 131 | 139 | 8 | 5 | 1 | 0 | closing flu damper
7.05 | 132 | 136 | 4 | 5 | 1 | 0
7.1 | 133 | 136 | 3 | 5 | 1 | 0 | Opened flu damper, built a new fire on a very nice bed of coals. Used quarters - mostly dry ash and walnut. Airflow a concern?
7.15 | 134 | 140 | 6 | 6 | 1 | 0
7.2 | 136 | 147 | 11 | 6 | 1 | 0
7.25 | 137 | 151 | 14 | 6 | 1 | 0
7.3 | 139 | 154 | 15 | 6 | 1 | 0
7.35 | 141 | 156 | 15 | 6 | 1 | 0
7.4 | 142 | 159 | 17 | 6 | 1 | 0
7.45 | 143 | 159 | 16 | 6 | 1 | 0
7.5 | 145 | 160 | 15 | 5 | 1 | 0
7.55 | 147 | 159 | 12 | 5 | 1 | 0
8 | 149 | 159 | 10 | 5 | 1 | 0
8.05 | 152 | 162 | 10 | 4 | 1 | 0
8.1 | 152 | 162 | 10 | 4 | 1 | 0
8.15 | 154 | 162 | 8 | 4 | 1 | 0
8.2 | 156 | 162 | 6 | 4 | 1 | 0
8.25 | 157 | 162 | 5 | 4 | 1 | 0
8.3 | 158 | 162 | 4 | 4 | 1 | 0
8.35 | 158 | 163 | 5 | 4 | 1 | 0 | flu damper still open - coals really kicking ass. Haven't opened the door ONCE this burn!
8.4 | 159 | 163 | 4 | 4 | 1 | 0
8.45 | 159 | 162 | 3 | 4 | 1 | 0
8.5 | 160 | 162 | 2 | 4 | 1 | 0
8.55 | 161 | 162 | 1 | 5 | 1 | 0
9 | 161 | 162 | 1 | 5 | 1 | 0 | closing flu damper

## heat calculation
We heated 260 gallons of water 70 degrees F in 6 hours.
heat required to heat 1 pound of water 1 degree farrenheit
gallons | lb/gal | lbs | degrees heated | net BTUs into water | time to do so (hours) | BTU/hr | 1 ton = | tons
260 | 8.2 | 2132 | 70 | 149240 | 6 | 24873.3333 | 12000 | 2.0728